## Slide 1
LESSON 01
Programmable Control
Fundamentals
Hardwired versus programmable control · PLC architecture · the scan cycle · IEC 61131-3
INS3150 · PLC Programming · Lesson 01
1
Notes: Open by naming the problem, not the syllabus. Every machine in the room is a control system. By the end of this lesson they should be able to say why a PLC replaced relay panels, and to trace one scan.

## Slide 2
Learning objectives
1
Explain what a control system is
open-loop, closed-loop, computerised
2
Compare hardwired with programmable control
and justify when each is appropriate
3
Describe the structure of a PLC
and the function of every internal block
4
Explain the S7-1200 memory areas
and read the CPU status LEDs
5
Trace the four phases of the scan cycle
and predict how they change behaviour
6
Identify the IEC 61131-3 languages
and the industry that favours each
INS3150 · PLC Programming · Lesson 01
2
Notes: Read these once, briefly. Do not dwell — they are a promise, and the lesson keeps it.

## Slide 3
1.1
What a Control System Is
Five elements appear in every control system, from a thermostat to a plant
INS3150 · PLC Programming · Lesson 01
3

## Slide 4
The five elements of any control system
Reference
sets the target
→
Measurement
observes reality
→
Comparator
finds the error
→
Controller
decides the action
→
Actuator
acts on the world
Every PLC program you will ever write is one of these blocks, or the logic that ties them together.
Reference input — the setpoint that starts the system: a temperature, a pressure, a level
Controlled variable — the quantity actually regulated at the output
Disturbance — anything that perturbs the signal, from inside or outside the system
INS3150 · PLC Programming · Lesson 01
4
Notes: Name all five before showing any PLC. Ask the room for the five blocks of a washing machine — it lands better than defining them abstractly.

## Slide 5
1.2
Open Loop, Closed Loop, Computerised
The same street lamp, wired two different ways
INS3150 · PLC Programming · Lesson 01
5

## Slide 6
One installation, two control philosophies
OPEN LOOP
Timer switch
Output does not affect the system
Lamps switch at a fixed hour
The controller never checks the sky
Simple to design
Accuracy depends on calibration
No instability — ever
CLOSED LOOP
Light sensor
Output feeds back and decides
Lamps follow actual brightness
The clock becomes irrelevant
Complex to design
Very accurate; rejects disturbance
Instability becomes possible
INS3150 · PLC Programming · Lesson 01
6
Notes: Draw the two block diagrams on the board rather than reading the list. The point to leave them with: closed loop is not automatically better — feedback buys accuracy and costs stability.

## Slide 7
1.3
Hardwired versus Programmable Control
In one, the logic lives in the wiring. In the other, in memory.
INS3150 · PLC Programming · Lesson 01
7

## Slide 8
Two workflows that diverge at step four
HARDWIRED
1
Define technology requirements
2
Design the control schematic
3
Select circuit elements
4
Wire and bond the elements
5
Test run and circuit test
PROGRAMMABLE
1
Define technology requirements
2
Design the algorithm
3
Draft the program
4
Load the program into memory
5
Test run and circuit test
INS3150 · PLC Programming · Lesson 01
8
Notes: Step four is the whole lesson. Everything before it is identical engineering; after it, one project needs a screwdriver and the other needs a download cable.

## Slide 9
1.4
Why Industry Switched
Two motors, one changed requirement, two very different bills
INS3150 · PLC Programming · Lesson 01
9

## Slide 10
The requirement changes: "also stop in sequence"
Relay panel
Schematic grows markedly more complex
Additional power devices required
The panel must be physically rewired
Machine stopped for the duration
PLC
Field wiring untouched
Edit the program
Download
New behaviour in service
You are not learning a programming language.
You are learning a way to make behaviour cheap to change.
INS3150 · PLC Programming · Lesson 01
10
Notes: This slide is the emotional centre of the lesson. Say the closing line slowly and let it sit before moving on.

## Slide 11
What that buys, in practice
Size
A cabinet of relays becomes one compact unit
Change
Modifications touch software, not wiring
Diagnosis
Built-in fault finding and forcing for commissioning
Networking
Standalone, networked, or a node in a distributed system
Civil use
LOGO-class units for lighting, ventilation, pumps
Industry
Lifts, production lines, robots, production data collection
INS3150 · PLC Programming · Lesson 01
11
Notes: Pick two of these and give a real example from a Vietnamese factory. Six abstract advantages are forgettable; one concrete story is not.

## Slide 12
1.5
Defining the PLC
NEMA, and the 1968 specification that started it
INS3150 · PLC Programming · Lesson 01
12

## Slide 13
The definition worth memorising
“A digitally operating electronic apparatus which uses a programmable memory for the internal storage of instructions — implementing functions such as logic, sequencing, timing, counting and arithmetic — to control machines and processes through digital or analogue input and output modules.”
National Electrical Manufacturers Association (NEMA)
1968 — General Motors wrote the specification
Easy to program
No rewiring to change function
Smaller and cheaper
High reliability
Simple construction, low maintenance
INS3150 · PLC Programming · Lesson 01
13
Notes: Point out that every one of the 1968 requirements still describes the unit on the bench. That is unusual for a 1968 specification and worth a beat.

## Slide 14
1.6
Structure of a PLC
A small purpose-built computer, block by block
INS3150 · PLC Programming · Lesson 01
14

## Slide 15
Inside the housing
Input module
switches · buttons · sensors
CPU module
processor + memory
Output module
lamps · contactors · motors
→
→
Bus system · address bus selects locations · data bus carries values · control bus synchronises
Power block
Typically 24 VDC. Some units run from 220 VAC; some have no power module and are supplied externally.
INS3150 · PLC Programming · Lesson 01
15
Notes: Hold up the real S7-1200 while showing this and point to each block on the physical unit. The diagram is abstract; the hardware in your hand is not.

## Slide 16
1.7
Memory and Status Indicators
Where the program lives, and how the CPU tells you what it is doing
INS3150 · PLC Programming · Lesson 01
16

## Slide 17
Memory is divided by purpose, not just by address
Program area
Instructions of your program
read / write
Parameter area
Passwords, station addresses, configuration
read / write
Data area
Results, constants, buffers — bit, byte, word, double word
dynamic
RAM holds the user program and is lost on power-down · ROM holds the system program and survives
INS3150 · PLC Programming · Lesson 01
17
Notes: Ask which area a tag value lives in versus where the compiled logic lives. It exposes whether they have really separated program from data.

## Slide 18
Reading the CPU status LEDs
SF
System fault
RUN
Executing the program
STOP
CPU halted
Ix.x
State of one input point
Qx.x
State of one output point
The I and Q LEDs show what the terminal actually sees — not what your program believes. Comparing the physical LED against the monitored tag separates a wiring fault from a logic fault in seconds.
INS3150 · PLC Programming · Lesson 01
18
Notes: Demonstrate live: force an output, show the Q LED change, then disconnect the field wire and show the LED still lit while the machine does nothing. That single demo teaches more than the slide.

## Slide 19
1.8
The Scan Cycle
Almost every beginner mistake traces back to this slide
INS3150 · PLC Programming · Lesson 01
19

## Slide 20
Four phases, repeating forever
1
Read inputs
Copy every DI and AI into the process image
→
2
Execute program
Run OB1 top to bottom against that image
→
3
Self-test
Internal communication and diagnostics
→
4
Write outputs
Copy the output image to the terminals
↻ the cycle repeats, and each pass is one scan
Your logic reads a snapshot — never a terminal changing mid-scan
An input that changes twice within one scan is seen once
An output written twice in one scan takes the value written last
Immediate I/O instructions bypass the image and suspend other work
INS3150 · PLC Programming · Lesson 01
20
Notes: Slow down here. Ask what happens to a 5 ms push-button pulse when the scan takes 12 ms. Let them work it out before you answer.

## Slide 21
Scan time is not fixed — and that has consequences
Scan time grows with program length and with the work done in a given pass.
A PLC is therefore unsuitable for control demanding hard microsecond determinism. Those tasks go to a dedicated high-speed counter, a PTO channel, or an FPGA — not to OB1.
Q
A button is pressed for 5 ms. The scan time is 12 ms. Does the program see it?
A
Not reliably. The press may fall entirely between two input-read phases. This is what hardware interrupts and high-speed counters exist for.
INS3150 · PLC Programming · Lesson 01
21
Notes: This is the slide students screenshot. Give them a moment before revealing the answer.

## Slide 22
1.9
Languages and Program Structure
Three notations for the same logic, and what runs when
INS3150 · PLC Programming · Lesson 01
22

## Slide 23
IEC 61131-3: same logic, three traditions
LAD
Ladder Diagram
Rungs and contacts, drawn like a relay schematic
Favoured by
Industrial electrical engineering
FBD
Function Block Diagram
Interconnected logic blocks
Favoured by
Electronics
STL
Statement List
Short mnemonics, like assembly language
Favoured by
Computing
None is more correct than the others. TIA Portal will show much of your program in whichever you choose.
INS3150 · PLC Programming · Lesson 01
23
Notes: Write the same AND rung in all three on the board. Seeing one piece of logic in three notations is the moment the standard stops being trivia.

## Slide 24
What runs, and when
Main program
Executes every scan
terminates with END
Subprogram
Called from the main program
terminates with RET
Interrupt routine
Runs when an event demands attention
terminates with RETI
S7-1200 I/O expands to the right of the CPU as a chain of SM, SB and CM modules · the engineering software is TIA Portal
INS3150 · PLC Programming · Lesson 01
24
Notes: Close the technical content here, then move straight to the review questions while attention is still high.

## Slide 25
Check yourself
1
Name the five elements of a control system, with a physical example of each
2
A street lamp switches on at 18:00 by timer. Open or closed loop — and what would make it the other?
3
What physically changes when "start in sequence" becomes "start and stop in sequence" — for a relay panel, and for a PLC?
4
Which memory area survives a power cycle, and which does not?
5
The RUN LED is green but the motor does not start. What can the CPU LEDs tell you before you open the program?
6
List the four scan phases in order, and explain why a short input pulse may be missed
INS3150 · PLC Programming · Lesson 01
25
Notes: Set these as the homework. Question 5 is the one that separates students who have understood diagnostics from those who have memorised slides.

## Slide 26
NEXT
Lesson 02 — S7-1200 Hardware
and TIA Portal
Device family · program processing · field wiring · installing and using TIA Portal
INS3150 · PLC Programming · Lesson 01
26
Notes: End on what comes next, and tell them to install TIA Portal before that session — the download is 10 GB.